Eaton Monitored ePDU Configuration Utility

Copyright (c) 2011 Eaton Corporation

Date: February 3, 2011

Version: 3.1A

1.0 DESCRIPTION	3

1.1 Installation	3

1.2 Usage	3

1.3 Requirements	3

2.0 UPLOADING FIRMWARE	3

2.1 Using the GUI	3

2.2 Using Command-Line Mode	4

3.0 INTERFACE COMMANDS	5

3.1 Browse…	5

3.2 Download	5

3.3 Search	5

3.4 Set IP Address	5

3.5 Ping: Ping Specific IP	6

3.6 Ping: Auto Ping List	6

3.7 Log: Log to File	6

3.8 Log: Export Log…	6

3.9 Log: Clear Log	6

4.0 FAQ	6

4.1 Can the use of broadcasts be disabled?	6

4.2 Is it possible to access ePDUs on remote segments?	6

4.3 Why do I get an error message when downloading to a specific ePDU?	7

5.0 WARNINGS	7

# 1.0 DESCRIPTION

## 1.1 Installation

The PC utility is named ePDUConfigMI.exe. There is no installation needed. It can run from anywhere.  The program uses an .ini file, ePDUConfigMI.ini, to store the last used firmware file location.

## 1.2 Usage

This program is meant to be used with Eaton Monitored ePDUs that have a blue/yellow LED display.  It has been tested and runs fine on Windows XP, Windows Vista, and Linux (under Wine).

## 1.3 Requirements

Only ePDUs on the local subnet will be accessible via the “Search” button.  For applications where the ePDU is on a remote subnet, use a laptop with a crossover cable and connect directly to the unit.

The downloader will work through a router if needed, but the search function will not work.  The “Ping Specific IP” command from the “Ping” menu can be used to find an ePDU on another subnet.  Alternatively, there is also an “Auto Ping List” command in the “Ping” menu.  This works similarly to the “Ping Specific IP” but allows a list of addresses to be searched automatically.

The “Ping Specific IP” command has been tested through firewalls.  A firewall needs to have UDP port 2000 forwarded to the ePDU.

# 2.0 UPLOADING FIRMWARE

## 2.1 Using the GUI

The utility will search for ePDUs upon startup.  It should find all ePDUs connected on the same local network segment.  If not, either the “Ping Specific IP” function or the “Auto Ping List” functions from the “Ping” menu may be needed as described earlier.  If no ePDUs are in the list, the utility will perform a broadcast search approximately every 10 seconds.

The ePDU list should show the ePDUs found.  If possible, the MAC address is shown.  If no ePDUs are in the list or the list needs to be updated, use the “Search” button.

To set the IP address of a unit, you should first select an ePDU from the list and then select the “Set IP Address” button.  The current IP address and MAC address of the unit will be automatically filled into the dialog.  Simply change the IP address and click “OK” to change the IP address.  Note that if the firmware is v1.0.L or earlier, changing the IP address from this utility is a temporary change; it must be made permanent by making the change again through the web or SNMP interfaces.

To download, you must first select one or more ePDUs from the list to download to and then press the “Download” button.  When multiple ePDUs are downloaded to, they are programmed sequentially.

The download will perform the following steps:

1. Send a “Run” command to start the ePDU’s RAM loader

2. Ping the ePDU to get a response from the RAM loader

3. Download the firmware onto the unit

4. Send a “Reboot” command to reboot the unit into the new firmware

Each step is acknowledged by the ePDU.  A progress bar on the top of the window shows download completion.

Once the download is complete and the ePDU has restarted, performing a new search will report the ePDU’s new firmware (for versions 1.0.J and later).

## 2.2 Using Command-Line Mode

The program may be executed from the command line as follows:

ePDUConfigMI /IP=ipaddr /ROM=image.bin

ipaddr – IP address of ePDU to download to

image.bin – The firmware program (may be in the current directory or a full path)

The program will return one of the following values, if there is an error.  It will also log to ePDUConfigMI.log on any command-line download.

Return values:

0 - Success

1 - Windows error

2 - /ROM not specified

3 - Could not find an ePDU at the specified IP

4 - Could not open firmware image

6 - Unspecified error

# 3.0 INTERFACE COMMANDS

## 3.1 Browse…

Use this button to browse to the firmware program that you want to upload to the unit(s).

## 3.2 Download

When clicked, the specified firmware will download to the selected unit(s) in the list.  If no units are selected in the list, it will display an error message.  NOTE: Pressing the download button with only one unit in the list will cause a download to that unit.  Because of this, an “Abort” button is available in case it is used accidentally.

## 3.3 Search

Whenever a search is performed, a broadcast ping is sent to the LAN on port 2000 which finds all units on the local network.  Again, this will not see past routers or firewalls on remote networks, unless port 2000 is forwarded (see: 4.2).  Search requests are also sent to each IP in the “Auto Ping List”.

## 3.4 Set IP Address

This command will change the IP address of the selected unit.  This command is generally used if there are multiple units on the same LAN with the same IP address or if a unit’s IP address is not correct for the current LAN.  This is especially useful for initial ePDU configuration.  Note that if the firmware is v1.0.L or earlier, changing the IP address from this utility is a temporary change; it must be made permanent by making the change again through the web or SNMP interfaces.

This dialog offers the option to direct the network packet to the unit’s MAC address (default) or to the unit’s IP address.  Directing it to the MAC address will only work on the local network segment, but it offers the capability of being able to change the IP address of a particular unit even though multiple units have the same default IP address.  Directing it to the IP address may be necessary in cases where the unit lies on a different network segment or where the ePDU is only running the RAM loader instead of the main firmware.

## 3.5 Ping: Ping Specific IP

This command is used for finding IP addresses that can’t normally be found using the “Search” button.  It will send search requests to specific IP addresses.  If an ePDU is remote and is accessible via the Internet, WAN, or LAN subnet, it can be searched for by IP address.

## 3.6 Ping: Auto Ping List

This command is similar to “Ping Specific IP”, except it automatically finds all listed IPs.  The list may contain an IP address, DNS name, or a file.  An entry such as “File:filename.ext” will have the program load the ping list from a separate file.  The file should be an unformatted text file with one IP address or DNS name per line.  The “Auto Ping List” is included for all searches, including when the “Search” button is pressed and when there are no units in the list.

## 3.7 Log: Log to File

Selecting this command will create (or append to) a log file called “ePDUConfigMI.log” in the directory where the program is located.  All future commands executed will be logged to this file, until the program is closed or until this command is selected again.  NOTE: This command will clear the current log shown at the bottom of the dialog!  If a user wishes to save the current log, they must select “Export Log…” first.

## 3.8 Log: Export Log…

This command will save the current log shown at the bottom of the dialog to a user-specified file.

## 3.9 Log: Clear Log

This command will clear the current log shown at the bottom of the dialog.

# 4.0 FAQ

## 4.1 Can the use of broadcasts be disabled?

Yes.  In the ePDUConfigMI.ini file, there is an option to disable the use of broadcasts.  This is:

No Search = 1

Use 1 to disable broadcasts, and 0 to enable broadcasts to discover ePDUs on the local segment.

## 4.2 Is it possible to access ePDUs on remote segments?

If an ePDU has a public IP, it can be accessed via the utility.  However, if it is behind a firewall or NAT router, the firewall or router needs to forward UDP port 2000.  For more information, try searching the internet for “port forwarding”.

## 4.3 Why do I get an error message when downloading to a specific ePDU?

If utility returns an error message similar to “The ePDU at IP address xxx.xxx.xxx.xxx does not respond to a ping to its IP,” then the IP address of the ePDU needs to be changed to one compatible with the PC.  Use the "Set IP Address" button to set the IP to one on the same LAN subnet as the PC.

# 5.0 WARNINGS

1. The utility verifies each operation.  It will try to recover from errors.  The status log window will show these errors.  The download can be retried if it fails.

2. Once the utility starts downloading firmware, the ePDU is susceptible to a power loss or reset.  If the ePDU is reset in the middle of a download, it may not recover!

3. Using the “Set IP Address” function will likely terminate any existing network connections to the ePDU.