Eaton ePDU

How to upgrade your ePDU Base Card Firmware & Network Management Card Firmware – 2-step Instruction File

7/28/2026

| Document Revision: | R11 |
| --- | --- |

Eaton Proprietary Information

Copyright © 2007 Eaton Corporation. All Rights Reserved.

Proprietary Notice

Copyright © 2007, 2008 Eaton Corporation. All Rights Reserved.

NOTICE TO PERSONS RECEIVING THIS DRAWING AND/OR TECHNICAL INFORMATION

Eaton Corporation claims proprietary rights to the material disclosed hereon.  This drawing and/or technical information is issued in confidence for engineering information only and may not be reproduced or used to manufacture anything shown or referred to hereon without direct written permission from Eaton Corporation to the user.  This drawing and/or technical information is the property of Eaton Corporation and is loaned for mutual assistance, to be returned when its purpose has been served.

THIS DRAWING AND/OR TECHNICAL INFORMATION IS THE PROPERTY OF EATON CORPORATION.

Revision History

| Revision | Who | Date | Notes |
| --- | --- | --- | --- |
| R00 | Vialle, JB | 2011 12 12 | First Draft |
| R01 | Vialle, JB | 2011 12 16 | Added note to avoid com conflict with hyper terminal or any other applications |
| R02 | Vialle, JB | 2012 02 16 | Updated with version 0002 of the upgrade tool and small addition |
| R03 | Vialle, JB | 2012 03 07 | Added upgrade note on one-time outlet reboot |
| R04 | Vialle, JB | 2012 03 07 | Added the NMC card upgrade procedure |
| R05 | Vialle, JB | 2012 03 09 | Minor corrections and re-layout |
| R06 | Vialle, JB | 2012 03 16 | Added revision information to help upgrade decision |
| R07 | Vialle, JB | 2012 08 02 | FW upgrade P5/30 to 00.10.0001 |
| R08 | Vialle, JB | 2012 11 08 | FW upgrade 3P to 00.12.0001 |
| R09 | Vialle, JB | 2013 03 15 | NMC FW new release 01.01.0009 |
| R10 | Vialle, JB | 2013 10 09 | NMC FW new release 01.01.0010 New release of base card 1P 01.12.0001 |
| R11 | Vialle, JB | 2014 03 04 | Bootloader Software Version: 00.01.0009 Firmware Software Version: 01.01.0011 Web Version: 01.01.0003 |

Table of content

A.	Introduction	5

1.1	Step 1 – ePDU Base Card Upgrade Instructions	7

1.2	Hardware and Preparation	8

1.3	Steps to follow to upgrade the ePDU	9

1.4	Install and use provided software for Firmware Upgrade	12

2.1	Step 2 – Network Management Card Upgrade Instructions	21

B.	Acronyms	30

Introduction

IMPORTANT - READ

Here is what you should know and remember first:

There are 2 independent sets of firmware accessible to upgrade:

- (Step 1) ePDU or also known as “Base Card” Firmware  Manages the data collection and management

- (Step 2) Com card or also known as “NMC” Firmware  Manages all communications to the outside

These 2 firmware are physically located inside to 2 different electronic cards (1 & 2 on the drawing below from managed unit):

1 - Base Card

Outlet Card

2 -

NMC

Outlet Card

Outlet Card

Input & Power

Com Ports

Circuit Breaker

Serial or

Ethernet

- You can elect to follow step 1 (Base Card) and/or step 2 (NMC) independently in the order that fits your needs:

  - Update recommended for Base Card firmware having a version below: 00.12.0001 (1P units)

  - Update recommended for Base Card firmware having a version below: 00.12.0001 (3P units)

  - Update recommended for NMC firmware having a version below: 01.01.0011

Note: You can find version information on the product LCD screen (Menu (ENTER) > ePDU Info > P3/5 (SCROLL)) or on the product web interface:

BC FW / NMC FW

Step 1

ePDU Base Card

UPGRADE PROCESS

## Step 1 – ePDU Base Card Upgrade Instructions

- General

This document is destined to the ePDU user that is willing to upgrade/flash his ePDU with a new ePDU base card firmware. This process can be performed while the ePDU’s outlets are “hot” and it will not affect their state. User must not in any case open the product for this upgrade. There is no safety risk to highlight. Please read carefully the information below;

- Important notes

- It is important that you close all programs on your connected PC or equipment while processing the instructions below;

## Hardware and Preparation

- For this operation, user need prepare tool as below:

- PC/laptop needs to have a serial port

Figure 1 - PC/Laptop serial port

- RS232 to RJ45 cable (use a USB adapter if you do not have a serial port on your laptop  not provided in product carton)

Figure 2 - Serial cable (comes with ePDU)

Figure 3 - USB adapter

- Upgrade software tool (setup.exe): “Eaton ePDU upgrade Software”

- Select the appropriate firmware file. There are 2 available file (*.S19) categories:

  - ICM1: 1-phase products

  - ICM3: 3-phase products

Example (file name for reference only):

## Steps to follow to upgrade the ePDU

Check upon

completion

Connect the RS232-RJ45 cable between the Computer (RS232) and the ePDU (RJ45 for serial).

Check upon

completion

Change the status of both switches from OFF to ON to switch to PDU upgrade mode.

Note: If both dip switches below are not toggled into OFF position, there will not be any serial communication and the upgrade will not be possible.

Warning: Do not change or touch dip switches during the upgrade process

Note: Be careful when changing the dip switches position as they are fragile. Do not use a sharp tool. Do not force them into position (verify if something is not blocking the switch)

Check upon

completion

Reset the NMC card with the button R available near the 2 switches.

- Note: Use a sharp long tool to press the recessed reset button during 1s to 3s.

- Note: After you do this, check that the 2 LEDs of the Serial port are OFF (2 arrows above).

Check upon

completion

Install and use provided software for Firmware Upgrade

Prerequisites : the upgrade software could be installed in Windows XP SP3 or higher release of Windows operating system.

You need to install the Eaton software upgrade tool on your PC.

- This tool (exe file) should be made available to you.

Figure 4 - Follow the step-by-step installation process

After correct installation (run setup.exe) of the Eaton software upgrade tool, double click the icon installed on your desktop or startup menu:

The below window opens:

Check upon

completion

Click the icon  to select the correct firmware *.s19 file, which you will flash into the ePDU (below picture is shown as an example).

Verify file path in main window:

Check upon

completion

Click the icon   ,wait for a moment, the tool window is updated with ePDU info as follows upon communication and connection success:

Check upon

completion

Click the icon  , then the ePDU begins the flash process as shown by the progress bar in the following window.

You can also check the ePDU LCD upgrade progress bar

- The upgrade time is about 5 minutes

Warning: Do not disconnect ePDU from mains or network connection during process – Avoid interactions on ePDU

Check upon

completion

Once flash upgrade is completed, you will see the following:

If the programming process is interrupted or unsuccessful, the following window is displayed:

- Re-execute Step 4 and try to perform the flash upgrade again. After several unsuccessful tries, contact Eaton support team or your local representative and escalate this issue

Check upon

completion

Flash Finish process:

Upon successful upgrade, change the dip switches to

1:”OFF”,2:”OFF” position as shown below:

Reset the card again and wait 30s. The user doesn’t need to restart the PDU.  This process should have had absolutely no impact on outlet state or connected loads.

Note: You can verify that you have the correct version of firmware on the LCD Screen with below process:

1) Press ENTER button

2) Select “ePDU info” on the menu screen (SCROLL down then ENTER)

3) Hit the SCROLL button twice and verify the ePDU FW Version is correct

4) Your ePDU is ready

Note: If firmware version is not correct and not matching the S19 file name, then try again following carefully the above process. You can try to force the upgrade by selecting the “Force Upgrade” check button:

Step 2

ePDU NMC

UPGRADE PROCESS

## Step 2 – Network Management Card Upgrade Instructions

Check upon

completion

Make sure that your ePDU is connected to the network via the Ethernet port of the ePDU:

Upgrade: Execute the firmware (.exe file) provided to you or downloaded from the web (visit www.eaton.com/ePDU).

If downloaded file is compressed, extract the content into your desktop folder or known location inside your PC and execute the program.

You do not need to restart your ePDU manually after the upgrade is complete.

Via ePDU dip switch:

Note:

- Note or remember the IP address of your ePDU as you not be able to retrieve it once in FTP mode

- The IP address in FTP mode is the same as in http mode.

Set the dip switch as below configuration;

Switch 1 = ON, Switch 2 = Off

Warning: Do not change or touch dip switches during the upgrade process

Note: The Switch 1 is closest to the serial port.

Then reset your ePDU via the recessed reset button and wait 30s

Note: To verify that the Com card is in FTP mode:
- Open a DOS window

- Then type "ftp IP address of the card" (i.e. “ftp 122.10.51.20”)

 Upon success you will read “Connected to XXX.XXX.XXX.XXX”

xxx.xxx.xxx.xxx

xxx.xxx.xxx.xxx

xxx.xxx.xxx.xxx

xxx.xxx.xxx.xxx

 Upon failure to connect, you will something similar to the following display

xxx.xxx.xxx.xxx

- Check your IP address is correct

- Check your dip switch setting as defined above

- Did you reset your com card and wait 30s?

- Do you have a working Ethernet connection between computer and ePDU?

- Restart the above procedure

- Contact Eaton support or local representative in case of permanent communication failure.

Check upon

completion

Upgrade: Execute the firmware (.exe file) provided to you or downloaded from the web (visit www.eaton.com/ePDU).

If downloaded file is compressed, extract the content into your desktop folder or known location inside your PC and execute the program.

Enter the IP address of the COM card in the DOS window (it may be different from the default address used below in example – i.e. 191.168.123.123):

- Enter the password "admin" and hit Enter key. The upgrade should start

Warning: Do not disconnect ePDU from mains or network during process

Wait for the upgrade to complete (~3min.) at the end you should have the following display after a successful upgrade:

(…)

Troubleshooting

- If communication is interrupted or having issues, retry this upgrade process.

- if:

- you have incorrectly positioned dip switches

- Connected the network cable in the wrong (i.e. serial port)

- Accidently disconnected the cable during upgrade (avoid at all cost)

You will likely have the following screen response:

In this case, make sure that you go back to this procedure and double check for mistakes

Here is a quick checklist:

- Communication with ePDU

  - ePDU power ON

  - Dip switches configuration

  - Incorrect IP address

  - Wrong port

  - Cable or connector issue

  - Environment disturbances (try in a  different location)

- FW version

  - Make sure that you have downloaded the latest version from the web

# Acronyms

| EMP | Environmental Monitoring Probe |
| --- | --- |
| ePDU | enclosure Power Distribution Unit |
| FW | Firmware |
| HW | Hardware |
| ICM | Input Connector Module (Also called the base card or mother board of the ePDU – 1 = 1-phase and 3 = 3-phase products) |
| NMC | Network Management Card (Project Name: Nemo) |
| SM | Section Module (Board that control and/or monitor the outlets) |

- END OF UPGRADE PROCESS -